## Slide 1: ASROCK RACK
Date: 10/ 27 /2020
1U12LW
FSC table

## Slide 2
Fan Control Algorithm
Environment Protection:
When Environment is 41。C , all of the fans will 100% duty.
Fan fail ( If one of the fans is fail, the others fans will 100% duty. )
Open loop
(Environment temperature )
Close loop
CPU
Initial PWM until BMC wake up
Start with Interval
1sec
Environment Protection
PWM Duty output
Compute
All Fan _PWM
Compare / Get Maximum duty
No
Yes
PWM MAX.Duty (100% duty)
Fan-1 star duty 30% Fan-2 star duty 30% Fan-3 star duty 30%
Fan-4 star duty 30%
Close loop
DIMM
Open loop
CPU

## Slide 3
Environment temperature open loop thermal control
M/B temp sensor Temperature (C) | Environment Temperature (C) | Fan Duty (%)
28 | 25 | 30
29 | 26 | 32
30 | 27 | 34
31 | 28 | 36
32 | 29 | 38
33 | 30 | 40
34 | 31 | 43
35 | 32 | 46
36 | 33 | 49
37 | 34 | 52
38 | 35 | 55
39 | 36 | 58
40 | 37 | 61
41 | 38 | 64
42 | 39 | 67
43 | 40 | 70
>=51 | >=41 | 100

## Slide 4
CPU Temperature (C) | Fan Duty (%)
70<= | 30
71 | 32
72 | 34
73 | 36
74 | 38
75 | 40
76 | 42
77 | 44
78 | 46
79 | 48
80 | 50
>=90 | 100
CPU open loop thermal control

## Slide 5
Fan duty increase by 1%/1sec
Fan duty no change
Fan duty decrease by 1%/3sec
CPU Close Loop
CPU Offset Temperature
CPU 85C
CPU 81C
低於 81度
減少duty 1%
每3秒執行一次
高於 85度
增加duty 1%
每1秒執行一次

## Slide 6
Fan duty increase by 1%/1sec
Fan duty no change
Fan duty decrease by 1%/5sec
DIMM Offset Temperature
DIMM 77C
DIMM Close Loop
DIMM 73C

## Slide 7
CPU Offset Rule
CPU Offset Rule |  |  |  | 
Step 1 : BMC read Tcc Target Temp from CPU |  |  |  | 
Step 2 : Offset = 98 - Tcc |  |  |  | 
Step 3 : New CPU Temp = DTS read from BMC + Offset |  |  |  | 
Step 4 : Send new CPU Temp to BMC |  |  |  | 
For Example : |  |  |  | 
130W CPU, Tcc Target Temp = 90 |  |  |  | 
Offset = 98 - 90=8 |  |  |  | 
If current CPU STS Temp = 80 |  |  |  | 
New CPU Temp = 80 + Offset = 80 + 8 = 88 |  |  |  | 
So, BMC will read 88 as FSC table reading, WebUI still show 80. |  |  |  | 

## Slide 8
Upper-non-critical-temperature alert and Upper-critical-temperature alert
Tempature | UNCT | UCT
Temp_CPU | Tjmax-1(92) | Tjmax(93)
Temp_DIMM | 84 | 85